FIRE & GAS DETECTION SYSTEM AUDIT CHECKLIST

A working audit checklist for HSE managers and maintenance teams

Applicable standards: SANS 10139  |  IEC 61511  |  IEC 61508  |  IEC 60079-29-0  |  IEC 60079-29-3

Frequency key:  M = Monthly   Q = Quarterly   A = Annual   3Y = Three-yearly     Tick the column(s) applicable when each item is verified.

| Facility: | ____________________________ | Audit Date: | ____________ |
| --- | --- | --- | --- |
| Plant / Unit: | ____________________________ | Work Order: | ____________ |

SECTION 1 — SYSTEM OVERVIEW VERIFICATION

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detection philosophy document is current, approved and available | ☐ | ☐ | ☐ | ☐ |
| Detection philosophy matches actual plant hazards and current layout | ☐ | ☐ | ☐ | ☐ |
| Cause and effect matrix is current and approved | ☐ | ☐ | ☐ | ☐ |
| Cause and effect matrix matches installed logic and outputs | ☐ | ☐ | ☐ | ☐ |
| As-built drawings are current and reflect actual installation | ☐ | ☐ | ☐ | ☐ |
| Detector index / I/O list is current | ☐ | ☐ | ☐ | ☐ |
| Detector location drawings match field installation | ☐ | ☐ | ☐ | ☐ |
| Last full system test date recorded | ☐ | ☐ | ☐ | ☐ |
| Last full system test certificate / report available | ☐ | ☐ | ☐ | ☐ |
| Open punch-list items from previous audit reviewed | ☐ | ☐ | ☐ | ☐ |
| Known inhibited / bypassed devices reviewed at start of audit | ☐ | ☐ | ☐ | ☐ |

SECTION 2 — DETECTOR INSPECTION CHECKLIST

2.1  Fixed Flammable Gas Detectors — Catalytic Bead and Infrared

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detector physically intact and securely mounted | ☐ | ☐ | ☐ | ☐ |
| Weather shield / splash guard present and intact where required | ☐ | ☐ | ☐ | ☐ |
| Sensor head clean and unobstructed | ☐ | ☐ | ☐ | ☐ |
| No painting, wrapping, bagging or temporary cover present | ☐ | ☐ | ☐ | ☐ |
| Detector label / tag number legible | ☐ | ☐ | ☐ | ☐ |
| Detector still located within intended gas cloud path / leak source coverage zone | ☐ | ☐ | ☐ | ☐ |
| No new piping, cladding, walls or cable trays affecting coverage | ☐ | ☐ | ☐ | ☐ |
| Calibration date current | ☐ | ☐ | ☐ | ☐ |
| Calibration gas and method appropriate for service | ☐ | ☐ | ☐ | ☐ |
| Bump / response test completed and satisfactory | ☐ | ☐ | ☐ | ☐ |
| Alarm setpoints match approved cause-and-effect / philosophy | ☐ | ☐ | ☐ | ☐ |
| Detector fault indications absent / investigated | ☐ | ☐ | ☐ | ☐ |
| Ex certification / hazardous area suitability remains valid for location | ☐ | ☐ | ☐ | ☐ |

2.2  Toxic Gas Detectors

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detector physically intact and securely mounted | ☐ | ☐ | ☐ | ☐ |
| Sensor inlet / membrane clean and unobstructed | ☐ | ☐ | ☐ | ☐ |
| Correct sensor type installed for target gas | ☐ | ☐ | ☐ | ☐ |
| Coverage remains valid for breathing zone / release scenario | ☐ | ☐ | ☐ | ☐ |
| Calibration current and traceable | ☐ | ☐ | ☐ | ☐ |
| Zero/span checks satisfactory | ☐ | ☐ | ☐ | ☐ |
| Functional response test satisfactory | ☐ | ☐ | ☐ | ☐ |
| Toxic alarm setpoints match approved basis | ☐ | ☐ | ☐ | ☐ |
| Detector life / cell expiry checked | ☐ | ☐ | ☐ | ☐ |
| Ex certification / hazardous area suitability remains valid | ☐ | ☐ | ☐ | ☐ |

2.3  Optical Flame Detectors — UV, IR, UV/IR, Multi-Spectrum IR

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detector housing intact and firmly mounted | ☐ | ☐ | ☐ | ☐ |
| Viewing window clean | ☐ | ☐ | ☐ | ☐ |
| Detector field of view unobstructed | ☐ | ☐ | ☐ | ☐ |
| No new equipment, scaffold, sheeting or pipework blocking line of sight | ☐ | ☐ | ☐ | ☐ |
| Detector orientation still matches design basis | ☐ | ☐ | ☐ | ☐ |
| Sunshade / weather shield intact where fitted | ☐ | ☐ | ☐ | ☐ |
| Detector not aimed into normal hot work zones without management controls | ☐ | ☐ | ☐ | ☐ |
| Detector not exposed to new false alarm sources (flare, exhaust, sunlight reflection, hot surfaces) | ☐ | ☐ | ☐ | ☐ |
| Functional test with approved simulator satisfactory | ☐ | ☐ | ☐ | ☐ |
| Alarm and fault outputs verified at controller / DCS | ☐ | ☐ | ☐ | ☐ |
| Ex certification / hazardous area suitability remains valid | ☐ | ☐ | ☐ | ☐ |

2.4  Smoke Detectors — Point Type and Beam Type

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detector / head physically intact | ☐ | ☐ | ☐ | ☐ |
| Detector location still appropriate for room use and airflow pattern | ☐ | ☐ | ☐ | ☐ |
| No dust build-up, paint contamination or physical obstruction | ☐ | ☐ | ☐ | ☐ |
| Point detector head clean and stable | ☐ | ☐ | ☐ | ☐ |
| Beam detector transmitter / receiver alignment verified | ☐ | ☐ | ☐ | ☐ |
| Beam path free of obstruction | ☐ | ☐ | ☐ | ☐ |
| Functional response test satisfactory | ☐ | ☐ | ☐ | ☐ |
| Alarm and fault conditions correctly reported | ☐ | ☐ | ☐ | ☐ |
| Certification / listing appropriate and still traceable | ☐ | ☐ | ☐ | ☐ |

2.5  Heat Detectors

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Detector physically intact | ☐ | ☐ | ☐ | ☐ |
| Detector free of paint, corrosion or mechanical damage | ☐ | ☐ | ☐ | ☐ |
| Location still appropriate for expected heat build-up area | ☐ | ☐ | ☐ | ☐ |
| No process change invalidating detector type or rating | ☐ | ☐ | ☐ | ☐ |
| Functional response test satisfactory | ☐ | ☐ | ☐ | ☐ |
| Alarm correctly reported at panel / controller / DCS | ☐ | ☐ | ☐ | ☐ |
| Certification / listing traceable | ☐ | ☐ | ☐ | ☐ |

2.6  Manual Call Points

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Manual call point visible, accessible and unobstructed | ☐ | ☐ | ☐ | ☐ |
| Signage present and legible | ☐ | ☐ | ☐ | ☐ |
| Housing / cover intact | ☐ | ☐ | ☐ | ☐ |
| Tag number / address correct and legible | ☐ | ☐ | ☐ | ☐ |
| Activation / reset test satisfactory | ☐ | ☐ | ☐ | ☐ |
| Device correctly reported at panel / controller / DCS | ☐ | ☐ | ☐ | ☐ |
| Certification / environmental suitability traceable | ☐ | ☐ | ☐ | ☐ |

SECTION 3 — CONTROL PANEL AND LOGIC CHECKLIST

| Item | M | Q | A | 3Y |
| --- | --- | --- | --- | --- |
| Fire and gas controller / panel healthy and free of standing faults | ☐ | ☐ | ☐ | ☐ |
| Panel enclosure clean, locked and protected from unauthorised access | ☐ | ☐ | ☐ | ☐ |
| Time and date correct on event history | ☐ | ☐ | ☐ | ☐ |
| Alarm, fault and supervisory indicators functioning | ☐ | ☐ | ☐ | ☐ |
| Power supply healthy | ☐ | ☐ | ☐ | ☐ |
| Battery backup test completed and satisfactory | ☐ | ☐ | ☐ | ☐ |
| Charger status normal | ☐ | ☐ | ☐ | ☐ |
| Event printer / historian / event log functioning where provided | ☐ | ☐ | ☐ | ☐ |
| Fault history reviewed for repeat defects | ☐ | ☐ | ☐ | ☐ |
| Alarm history reviewed for nuisance alarms / chattering signals | ☐ | ☐ | ☐ | ☐ |
| DCS interface verified | ☐ | ☐ | ☐ | ☐ |
| ESD interface verified | ☐ | ☐ | ☐ | ☐ |
| Deluge / suppression output interfaces verified where fitted | ☐ | ☐ | ☐ | ☐ |
| Hooters / beacons / visual alarms correctly mapped | ☐ | ☐ | ☐ | ☐ |
| Inhibit register current and reviewed | ☐ | ☐ | ☐ | ☐ |
| Overrides / bypasses authorised and time-bounded | ☐ | ☐ | ☐ | ☐ |
| Any inhibited detector linked to active work order / permit | ☐ | ☐ | ☐ | ☐ |
| Cause-and-effect sample test completed satisfactorily | ☐ | ☐ | ☐ | ☐ |
| Full end-to-end logic validation scheduled / completed | ☐ | ☐ | ☐ | ☐ |

SECTION 4 — FREQUENCY REFERENCE TABLE

| Frequency | Typical Activities |
| --- | --- |
| Monthly | Visual inspection of all detectors and panels; check for obstruction, damage, panel faults, inhibited devices, obvious documentation gaps |
| Quarterly | Functional checks on selected detectors/devices; review fault/alarm trends; sample response tests; verify interfaces on a sample basis |
| Annual | Formal calibration programme; wider functional testing; panel battery checks; detector coverage review against current plant layout; drawing and register reconciliation |
| Three-yearly | Full system functional test: end-to-end cause-and-effect validation; interface verification; representative field response testing; formal review of whether detector placement still matches process hazards |

Where the site SRS, insurer, OEM or statutory framework requires tighter intervals, that requirement takes precedence.

SECTION 5 — COMMON NON-CONFORMANCES TO LOOK FOR

| Non-Conformance | Found | Not Found |
| --- | --- | --- |
| Detectors painted over | ☐ | ☐ |
| Detector face / optics physically obstructed | ☐ | ☐ |
| Detector covered during maintenance and not returned to service | ☐ | ☐ |
| Expired calibration certificates | ☐ | ☐ |
| Incorrect or unavailable calibration gas | ☐ | ☐ |
| Inhibited detectors with no active work order | ☐ | ☐ |
| Missing or damaged weatherproof housings / shields | ☐ | ☐ |
| Undocumented system modifications | ☐ | ☐ |
| Detector tag number missing or mismatched to drawings | ☐ | ☐ |
| Detector placement no longer valid due to process or layout change | ☐ | ☐ |
| Repeat nuisance alarms not investigated | ☐ | ☐ |
| Alarm setpoints changed without approval record | ☐ | ☐ |
| As-built drawings do not match the field | ☐ | ☐ |
| Ex certificate or hazardous area suitability cannot be traced | ☐ | ☐ |

AUDIT SIGN-OFF

| Facility Name | ________________________________________ |
| --- | --- |
| Plant / Unit | ________________________________________ |
| Audit Date | ________________________________________ |
| Audit Type | ________________________________________ |
| Auditor Name | ________________________________________ |
| Auditor Signature | ________________________________________ |
| Responsible Site Representative | ________________________________________ |
| Next Audit Due Date | ________________________________________ |

Immediate critical actions required before return to normal operation:

______________________________________________________________________________

______________________________________________________________________________

Disclaimer: This checklist is provided for general guidance only. It does not constitute engineering advice and does not replace the applicable standards, site-specific engineering judgement, or the involvement of a qualified and registered engineer. Touch Teq Engineering accepts no liability for any loss, damage or non-compliance arising from the use of this document. Always refer to the current edition of the applicable standards.